## Calculator
Hazen-Williams head loss (SI)
Inputs
Flow | 20 | L/s
Internal diameter | 150 | mm
Pipe length | 1200 | m
Material | Ductile iron, cement-lined | pick from the list
C from table | 140
C override (optional) |  | leave blank to use the table
C used | 140
Results
Flow Q | 0.02 | m³/s
Diameter d | 0.15 | m
Head loss hf | 9.9768 | m of water
Head loss per km | 8.314 | m/km
Pressure loss | 97.8719 | kPa
Pressure loss | 14.1899 | psi
Velocity | 1.1318 | m/s
Check | OK
Same pipe, other C values
Head loss at C = 150 | 8.7801 | -11.99%
Head loss at C = 130 | 11.4445 | 14.71%
Head loss at C = 110 | 15.5941 | 56.3%
Head loss at C = 100 | 18.6045 | 86.48%
Same pipe, other published constants
10.67, d^4.87 | 9.9692 | m
10.667, d^4.871 (EPANET) | 9.9853 | m
10.67, d^4.8704 (B14) | 9.9768 | m

## US units
Hazen-Williams in US units (NFPA 13 form)
Inputs
Flow | 6 | gpm
Internal diameter | 0.785 | in (3/4" type L copper)
Pipe length | 100 | ft
C | 130 | copper, lower end
Elevation rise | 15 | ft (meter to highest fixture)
Static pressure at start | 60 | psi
Results
Friction loss per foot | 0.049649 | psi/ft
Friction loss | 4.9649 | psi
Friction loss as head | 11.453 | ft of water
Elevation loss | 6.5025 | psi
Residual pressure | 48.5326 | psi
Velocity | 3.9774 | ft/s
Check | OK
Cross-check: the SI example in US units
Flow | 317.0065 | gpm
Internal diameter | 5.9055 | in
Pipe length | 3937.008 | ft
NFPA friction loss | 14.1553 | psi
NFPA result in metres | 9.9524 | m of water
SI result (Calculator!B14) | 9.9768 | m of water
Difference | -0.244%

## Solve for
Solve Hazen-Williams for flow or diameter (SI)
Flow a pipe can carry
Allowable head loss | 5 | m
Pipe length | 1200 | m
Internal diameter | 150 | mm
C | 140
Flow | 13.7731 | L/s
Velocity | 0.7794 | m/s
Diameter you need
Flow | 20 | L/s
Allowable head loss | 5 | m
Pipe length | 1200 | m
C | 140
Minimum internal diameter | 172.8589 | mm: round up to a real size
Check: hf at that diameter | 5 | m (should equal B13)

## Pipe run
Pipes in series: residual head at the end
Segments (leave unused rows blank)
Segment | Flow (L/s) | ID (mm) | Length (m) | C | hf (m) | Velocity (m/s)
Trunk main | 30 | 200 | 800 | 140 | 3.4715 | 0.95493
Distribution main | 20 | 150 | 600 | 140 | 4.9884 | 1.1318
Branch | 8 | 100 | 400 | 140 | 4.3905 | 1.0186
Head at the start | 45 | m
Elevation rise to the end | 12 | m
Total friction loss | 12.8504 | m
Residual head at the end | 20.1496 | m
Residual pressure | 197.6674 | kPa

## C values
Material | C used | Range | Source
PVC | 150 | 150 | Wikipedia; EngineerExcel
Polyethylene (PE/HDPE) | 140 | 140 | Wikipedia
Copper | 135 | 130-140 | Wikipedia
Ductile iron, cement-lined | 140 | 140 | Wikipedia; EngineerExcel
Cast iron, new | 130 | 130 | Wikipedia
Cast iron, 10 years old | 110 | 107-113 | Wikipedia
Cast iron, 20 years old | 95 | 89-100 | Wikipedia
Asbestos-cement | 140 | 140 | Wikipedia
Concrete | 120 | 100-140 | Wikipedia
Steel | 120 | 90-120 | Wikipedia
Galvanized iron | 120 | 120 | Wikipedia
Use your utility's or code's design value where one applies (e.g. NFPA 13 tables for sprinklers).

## HW vs Darcy
Hazen-Williams vs Darcy-Weisbach (PVC, % difference)
Water temperature | 20 | °C
Kinematic viscosity | 1.0168 | mm²/s
Hazen-Williams C | 150
Roughness ε (mm) | 0.0015
ID (mm) \ velocity (m/s) | 0.3 | 1 | 2 | 3
20 | -20.77% | -8.298% | -2.657% | 0.03792%
50 | -12.18% | -1.932% | 2.464% | 4.47%
100 | -6.903% | 1.67% | 5.165% | 6.682%
200 | -2.675% | 4.284% | 6.932% | 7.992%
500 | 1.381% | 6.339% | 7.961% | 8.477%
Positive: Hazen-Williams gives more loss than Darcy-Weisbach.
Hot-water check: 25 mm PVC at 1.5 m/s
Temperature (°C) | 20 | 60
Viscosity (mm²/s) | 1.0168 | 0.4694
HW vs Darcy | -3.306% | 14.05%